## Sheet1
Parameter | Design | October | November | December | January | February | March | Performance | Extra | Calculated Performance | % Deviation | Significant Deviation | Recommendation
Steam Pressure at Boiler Outlet (kg/cm2) | 170 | 161.4957 | 158.4525 | 158.7288 | 149.6515 | 160.1574 | 160.0301 | 161.4957 |  | 161.4957 | -5.0025 | TRUE | Low pressure, investigate combustion or flow
Steam Temperature at Boiler Outlet (°C) | 537 | 536.0012 | 535.7647 | 535.2988 | 510.3294 | 535.9414 | 536.8858 | 536.8858 |  | 536.8858 | -0.021271 | FALSE | OK
Ash Content in Coal (%) | 40 | 41.7109 | 41.006 | 41.4054 | 40.2674 | 40.8376 | 41.9691 | 40.2674 |  | 40.2674 | 0.66843 | FALSE | Review coal quality and combustion process
Total Air flow at APH Outlet (TPH) | 1938 | 2047.7794 | 2008.1787 | 2033.7545 | 1907.8729 | 1996.9081 | 2015.9107 | 1907.8729 |  | 1907.8729 | -1.5545 | FALSE | Inspect flow controls, fans, ducts
Feed Water Flow Rate (TPH) | 1799.59 | 1838.1929 | 1809.7792 | 1812.4336 | 1711.3506 | 1830.3777 | 1807.5521 | 1807.5521 |  | 1807.5521 | 0.44244 | FALSE | Inspect flow controls, fans, ducts
Fuel Gas Temperature (°C) | 135 | 135.464 | 130.4503 | 129.89 | 121.9966 | 132.1739 | 135.3585 | 135.3585 |  | 135.3585 | 0.26555 | FALSE | OK